## Sheet1
ID | Text
3_Finnish_Accessibility | There shall be an easily noticeable passageway with a width of at least 1,200 millimetres and a smooth, hard and non-slippery surface that leads to the building from the boundary of the plot or building site and from the space and area that serve the use of the building.
4_Finnish_Accessibility | The gradient of the passageway located in an outdoor space may not exceed five per cent.
5_Finnish_Accessibility | If there are steps on the passageway, there shall also be a ramp or a permanently installed device intended for lifting persons that is suitable for a user of a wheelchair and walking frame with wheels.
7_Finnish_Accessibility | There shall be a horizontal landing with a length of at least 1,500 millimetres at the lower and upper end of the ramp.
8_Finnish_Accessibility | The gradient of the ramp may not exceed five per cent.
15_Finnish_Accessibility | The distance of the opening side of the outside door of a building from the inside corner of the wall or other fixed obstacle outside the door shall be at least 400 millimetres.
16_Finnish_Accessibility | The landing in front of the outside door shall be at least 1,500 millimetres wide and at least 1,500 millimetres long.
22_Finnish_Accessibility | The outside door of a building and the door of a space serving the use of the building shall function so that it is easy to open by a person with mobility and functional impairment.
24_Finnish_Accessibility | Passageway inside a non-residential building and common spaces of a residential building shall be easily noticeable and have a smooth and non-slippery surface.
27_Finnish_Accessibility | Spaces of a non-residential building and common spaces of a residential building as well as the fixtures, fittings and fixed equipment in them shall be suitable for persons with mobility and functional impairment.
29_Finnish_Accessibility | A dwelling that is intended for service housing or supported housing of a person with mobility and functional impairment shall, irrespective of the number of storeys in the building, have a turning space with a diameter of at least 1,500 millimetres in the hallway and kitchen.
32_Finnish_Accessibility | In addition to stairs, a residential building shall also be equipped with a lift if entry to a dwelling in the building is on the third floor or higher, the entrance floor level included.
33_Finnish_Accessibility | The lift shall provide access to the entrance level and each level with entry to a dwelling or a space serving the use of the building.
40_Finnish_Accessibility | The fixtures and fittings shall be placed with respect to the free space so that a person with mobility impairment can use them.
41_Finnish_Accessibility | The toilet and washing facility shall be such that it can be equipped to be suitable for use by a person with mobility impairment.
42_Finnish_Accessibility | A dwelling that is intended for sheltered housing or supported housing of a person with mobility or functional impairment shall have at least one toilet and washing facility which has a free space with a diameter of at least 1,500 millimetres.
43_Finnish_Accessibility | The fixtures and fittings shall be placed with respect to the free space so that a person with mobility impairment can use them.
45_Finnish_Accessibility | The toilet and washing facility shall be such that it can be equipped to be suitable for use by a person with mobility impairment.
48_Finnish_Accessibility | In a residential building the sauna, washing and changing facility common to all residents shall be suitable for persons with mobility and functional impairment.
51_Finnish_Accessibility | A non-residential building shall, considering the intended use and functional units of the building and distances in the building, have an adequate number of appropriately located toilet facilities which are suitable for users of wheelchairs and walking frames with wheels.
54_Finnish_Accessibility | The fixtures and fittings shall be placed with respect to the free space so that a person with mobility impairment can use them.
57_Finnish_Accessibility | The toilet seat shall be placed between 200 and 300 millimetres from the rear wall.
58_Finnish_Accessibility | The toilet facility shall be equipped to be suitable for use by a person with mobility impairment.
59_Finnish_Accessibility | If the building has a control system, the toilet facility shall have a security alarm connection to the control.
62_Finnish_Accessibility | The facilities suitable for persons with mobility and functional impairment shall be marked with the International Symbol of Access.
63_Finnish_Accessibility | If the building has a control system, the facilities suitable for persons with mobility and functional impairment shall have a security alarm connection to the control.
67_Finnish_Accessibility | Any sound system in an auditorium, a restaurant, a conference facility, a facility for festive occasions, a teaching facility or other similar assembly facility or a public service facility shall have an induction loop or a similar sound transmission system.
70_Finnish_Accessibility | In a hotel building and other similar accommodation building, at least five per cent of the accommodation rooms, but at least one accommodation room, shall be suitable for persons with mobility and functional impairment and their assistants.
12_Finnish_AcousticEnvironment | The noise and vibration at the site of the building shall be taken into account in the design and construction of the building.
17_Finnish_AcousticEnvironment | In rooms used for sleeping or rest, the one-hour A-weighted equivalent continuous sound level of impulsive, narrow-band or low-frequency noise may not exceed 25 decibels.
19_Finnish_AcousticEnvironment | The sound insulation of recessed balconies, conservatories and roof terraces shall be designed and implemented so that the acoustic environment does not cause any inconvenience to the residents.
21_Finnish_AcousticEnvironment | The sound insulation of the envelope of a building with dwellings or accommodation or patient rooms shall be designed and implemented so that the sound insulation is at least 30 decibels and the A-weighted equivalent continuous sound level of impulsive, narrow-band or low-frequency noise in rooms used for sleeping or rest does not exceed 25 decibels.
26_Finnish_AcousticEnvironment | A building with dwellings or accommodation or patient rooms shall be designed and implemented so that the reverberation time of the staircase and exit route is no more than 1.3 seconds.
27_Finnish_AcousticEnvironment | Yards and spaces intended for use by residents of a building and balconies used by residents shall be designed and implemented so that the A-weighted equivalent continuous sound level between 7.00 and 22.00 does not exceed 55 decibels and, similarly, conservatories so that the A-weighted equivalent continuous sound level does not exceed 45 decibels.
29_Finnish_AcousticEnvironment | Repair or alteration work of a building shall not weaken the sound insulation, noise and vibration abatement or acoustic conditions of the building or the noise abatement or acoustic conditions of yards, spaces intended for use by residents and balconies used by residents.
59_Finnish_EnergyEfficiency | Calculations shall take place using a calculation method taking at least the following factors into account: a) the thermal characteristics of building elements and their connections, the buildings airtightness, ventilation air flow; b) indoor air temperature; c) the demand for domestic hot water; d) ventilation heat recovery; e) the thermal loads from humans, lighting, electrical appliances, domestic hot water and sunlight; f) the heat and electrical energy demand of the space and ventilation heating system; g) the heat and electrical energy demand of the domestic hot water preparation system; h) the electrical energy demand of the ventilation system; i) the electrical energy demand of consumer equipment and lighting.
60_Finnish_EnergyEfficiency | The building's calculated consumption of delivered energy may be calculated using the monthly calculation method for buildings the indoor air temperature control of which does not require cooling or where cooling is only required for spaces the net heated area of which is less than 10 of the buildings net heated area or the net heated area of which is less than 50 m2.
67_Finnish_EnergyEfficiency | The outdoor air flow used in the calculations for buildings other than those in intended use categories 1 and 2 outside the occupancy period shall be at least 0.15 dm3/s per m2.
84_Finnish_EnergyEfficiency | The net heating energy demand for a buildings spaces shall be calculated on the basis of conduction loss, leakage air heat loss and the heating of replacement air and supply air in the space to room temperature, less the impact of the sun and internal thermal loads.
85_Finnish_EnergyEfficiency | Any solar protection solutions in the building shall be taken into account in the calculation of solar energy gains for the building.
86_Finnish_EnergyEfficiency | The net heating energy demand for ventilation shall be calculated on the basis of the heating of air after heat recovery to supply air temperature and any heating before heat recovery.
91_Finnish_EnergyEfficiency | The impact of the ground and crawl space on heat loss shall be taken into account in heat loss calculations.
101_Finnish_EnergyEfficiency | If the building is connected to a heating system where heat is conveyed via heat pipes external to the building from a shared heat exchanger or heat generation unit to several buildings, the heat loss from those pipes shall be divided between the buildings in proportion to their areas.
103_Finnish_EnergyEfficiency | If the circulation piping is located inside the building envelopes insulation, 25 of the calculated domestic hot water circulation heat loss shall be added to the thermal load of the spaces of the building.
104_Finnish_EnergyEfficiency | If the circulation piping is located inside the building envelope, 50 of the calculated domestic hot water circulation heat loss shall be added to the thermal load of the spaces of the building.
105_Finnish_EnergyEfficiency | If the domestic hot water cylinder is located inside the building envelope, 50 of the calculated domestic hot water cylinder heat loss shall be added to the thermal load of the spaces of the building.
109_Finnish_EnergyEfficiency | The electrical energy consumption of a mechanical ventilation system shall be calculated on the basis of air flows, specific fan powers and operating times for all air handling units and powered roof ventilators in the building.
111_Finnish_EnergyEfficiency | When calculating the energy consumption of a buildings cooling system, the energy consumption of cooling energy production and the electrical energy consumption of auxiliary units shall be taken into account where the use of the systems is required for indoor temperature control.
124_Finnish_EnergyEfficiency | The reference value for a building's total combined window area is 15 of the sum total of the floor plate areas of the buildings storeys that are fully or in part above the ground but, however, at most 50 of the building's facade area.
136_Finnish_EnergyEfficiency | When calculating the reference heat loss of a building, the value of 2.0 m3/(h m2) shall be used as the reference value for the air leakage rate figure for the building envelope.
137_Finnish_EnergyEfficiency | When calculating the heat loss for a buildings design solution, the design value shall be used as the value of the air leakage rate figure for the building envelope.
151_Finnish_EnergyEfficiency | In reference heat loss calculations, the value used as the annual efficiency of heat recovery from ventilation extract air of the buildings ventilation system shall be 55.
157_Finnish_EnergyEfficiency | To prevent ground frost damage, ground frost insulation and any thermal insulation of foundation walls not included in the building envelope shall be taken into account in the design of thermal insulation for a buildings base floor.
162_Finnish_EnergyEfficiency | A dynamic calculation tool shall be used for the calculation of the room temperature for the summer season.
172_Finnish_EnergyEfficiency | An energy declaration shall be drawn up when designing a building.
26_Finnish_FireSafety | An exit enclosure has doors that open separately into each adjoining fire compartment without a need to open the doors at the same time.
56_Finnish_FireSafety | An area with a potentially flammable or explosive atmosphere must not be located in a building where there are dwellings, accommodation premises, institutions or assembly and business premises.
68_Finnish_FireSafety | If necessary, the mean height of the buildings corner points shall be calculated.
69_Finnish_FireSafety | In a building consisting primarily of one storey, no more than 200 m2 of fire-compartmented and no more than 50 m2 of non-fire-compartmented areas that essentially relate to the business of the building may be located on the level of second storey.
72_Finnish_FireSafety | In a building consisting primarily of one storey, no more than 200 m2 of fire-compartmented and no more than 50 m2 of non-fire-compartmented areas that essentially relate to the business of the building may be located on the level of second storey.
73_Finnish_FireSafety | Storage premises with a fire load exceeding 1,200 MJ/m2 are not permitted within the building.
75_Finnish_FireSafety | If the building comprises premises of different categories of use, the safety level of the building shall be assessed by considering the building as a whole.
82_Finnish_FireSafety | Technical installations shall be made in such a way that the hazards of ignition of fire and spread of fire and smoke within the building is not essentially increased thereby.
83_Finnish_FireSafety | Fire-places, chimneys and heating devices shall be located and built or installed in such a manner that their use will not create a hazard of fire or explosion.
87_Finnish_FireSafety | If necessary for the safety of people or with regard to the extent of the damage, the building must sustain the combustion of the entire fire load and the cooling phase without collapse.
88_Finnish_FireSafety | If a load-bearing element is required to have a longer fire resistance time with respect to integrity E and insulation I than with respect to load-bearing capacity R, the longer fire resistance time shall also be applied to the load-bearing capacity.
90_Finnish_FireSafety | The fire resistance time requirement for balconies is half that of the load-bearing structures of the storey.
101_Finnish_FireSafety | The various storeys, basement storeys and the attic of a P1 and P2 fire class building must be made into separate fire compartments (fire compartmentation by storey), and the same applies to the basement storeys of fire class P3 that serve more than one apartment.
102_Finnish_FireSafety | A fire compartment may, however, comprise several storeys, excluding compartments with rooms for accommodation or patient rooms, with the following restrictions: 1) in a building whose height exceeds 28 metres, no more than two storeys above this height of 28 metres may comprise a single fire compartment, excluding the staircase, and the size of a single fire compartment must not exceed 2,400 square metres; and 2) at a height of over 56 metres, a fire compartment is restricted to a single storey, apart from residential apartments, where two-storey fire compartments are permitted, and staircases.
106_Finnish_FireSafety | If necessary, fire compartments shall be partitioned in order to restrict the spread of fire and smoke, to provide safe evacuation and to facilitate rescue and extinguishing measures.
107_Finnish_FireSafety | Attics and uppermost floor voids shall be divided into 400 m2 parts.
258_Finnish_FireSafety | The fire compartment shall be partitioned by accommodation room.
110_Finnish_FireSafety | In an open garage of no more than five storeys, the maximum area may be used as the surface area of the storeys, even though the driveways between the various storeys are combined.
118_Finnish_FireSafety | A fire door must be self-closing and self-bolting.
120_Finnish_FireSafety | If a fire door is kept open in normal use, it shall be equipped with devices that will close the door in the event of fire.
121_Finnish_FireSafety | Partitioning doors in accommodation premises shall be equipped with closing devices.
123_Finnish_FireSafety | Pipes, shafts, ducts, cables and flues, and penetrations required by conveyors that are mounted through a fire-separating building element must not essentially reduce the fire compartmenting capacity of the building element.
125_Finnish_FireSafety | The ventilation system must not increase the hazard of spreading fire or gaseous combustion products.
128_Finnish_FireSafety | Attics and voids shall be built in such a way that the hazard of ignition of fire and spread of fire and smoke within the building is not essentially increased thereby.
129_Finnish_FireSafety | Extensive voids must be partitioned in order to restrict the spread of fire.
130_Finnish_FireSafety | The spread of fire in voids of wall-type building elements must be restricted at least by storey.
133_Finnish_FireSafety | In glazed balconies, the spread of fire from one balcony to another and to an adjacent fire compartment must be restricted.
156_Finnish_FireSafety | The fire performance of the external wall structure of a building no more than 56 metres in height may also be demonstrated by a fullscale test.
178_Finnish_FireSafety | A roof must not easily ignite from a fire at a neighbouring building.
181_Finnish_FireSafety | Large roof surfaces must be divided into parts of no more than 2,400 square metres.
189_Finnish_FireSafety | A building must be provided with a fire wall if it is situated adjacent to a neighbouring building or so close to a neighbouring building that the spread of fire is evident.
201_Finnish_FireSafety | If the passageways to two separate exits partly join, the length of the common part must be doubled in the calculation.
209_Finnish_FireSafety | Exits of parts of the building separated by a fire wall must be constructed separately so that in the event of a fire there is no need to use any door that may be in the fire wall.
214_Finnish_FireSafety | The width of an exit must be at least 1,200 millimetres and its free height must be at least 2,100 millimetres.
216_Finnish_FireSafety | in an evacuation area where the maximum number of occupants is 60, the second exit may be no less than 900 millimetres in width.
217_Finnish_FireSafety | in residential buildings of not more than two storeys, one exit of no less than 900 millimetres in width is permitted.
218_Finnish_FireSafety | If a lift or other device for moving between levels is installed in the exit of an existing building, the dwellings exit may be no less than 850 millimetres wide.
219_Finnish_FireSafety | If the number of occupants exceeds 120, the total minimum width of the exits shall be calculated by increasing the original 1,200 millimetres by 400 millimetres for each additional group of 60 people.
222_Finnish_FireSafety | The doors of exits, and of areas leading to them, must be easy to open in an emergency.
223_Finnish_FireSafety | In the case of the storey-level door of a dwelling, or if the number of people evacuating through the door exceeds 60, doors must open in the direction of the exit.
229_Finnish_FireSafety | Dwellings, accommodation premises, institutions, day-care institutions, day-care centres and other early childhood education premises and schools must be provided with an appropriate system that gives a warning at an early stage of a beginning fire.
232_Finnish_FireSafety | There must be an automatic fire-extinguishing system that is suitable for its purpose and connected to the emergency centre.
239_Finnish_FireSafety | It must be possible for fire and service rescue equipment to have sufficiently close access to the building (emergency access road).
240_Finnish_FireSafety | There must be access to each fire compartment of an attic for firefighting operations.
241_Finnish_FireSafety | If the height of the building does not exceed 28 metres, access to the attic fire compartments from the outside shall be required.
242_Finnish_FireSafety | Extinguishing routes to basement storeys shall be arranged so that basement storeys can be reached from the ground level without a need to pass through the exits of the storeys.
244_Finnish_FireSafety | Extinguishing routes of basement storeys must not be connected to fire and smoke-proof exits.
246_Finnish_FireSafety | A lift must be available for use in rescue and extinguishing work (firefighting lift); 1) in areas above the entrance level when the distance of the floor of the uppermost storey exceeds 38 metres from the buildings entrance level; 2) in areas below the entrance level when the distance of the floor of the basement storey exceeds 14 metres from the buildings entrance level and the surface area of that basement storeys evacuation area exceeds 800 m2.
249_Finnish_FireSafety | In order to enhance the efficiency of firefighting and rescue operations, means of smoke extraction shall be designed and constructed in the building so that smoke can be extracted from the different premises in the building.
250_Finnish_FireSafety | In exit passageways and fire-compartmented elevator shafts, means must be arranged for both smoke extraction and flow of replacement air.
254_Finnish_FireSafety | A building shall be provided with a permanently installed dry riser that is suitable for its purpose for transporting water for fire extinguishing: 1) in the premises above the entry level of the building, when the distance of the uppermost floor level from the entry level exceeds 24 metres; 2) in the premises below the entry level of the building, when the distance of the basement storey floor from the entry level exceeds 14 metres.
34_Finnish_Health-Humidity | The buildings enclosure together with its construction layers and joints must form a whole, preventing the transfer of water across the surface of the enclosure into the construction by wind, slanting rain and wind pressure.
35_Finnish_Health-Humidity | Building moisture and internal or external moisture transferred occasionally to the structures must be able to escape without causing damage.
36_Finnish_Health-Humidity | Structures with surfaces exposed to moisture must be resistant to the effects of water.
40_Finnish_Health-Humidity | The ventilation openings or slots leading to the ventilation space or gap of a structure equipped with a ventilation space or gap must be positioned so that the ventilation space or gap is fully usable as a ventilation air flow path and that the ventilation space or gap is free of enclosed, non-ventilated areas.
45_Finnish_Health-Humidity | Humus soil, organic substances decomposing or rotting from moisture or building waste must not be left under new buildings, in their crawl spaces and in their gravel backfills functioning as a drainage layer.
50_Finnish_Health-Humidity | Water must not freeze in the systems pipes, channels or devices.
51_Finnish_Health-Humidity | Condensed water on the systems pipes, channels or devices must not cause harm or the condensed water must be removable without causing damage.
79_Finnish_Health-Humidity | No water must accumulate in the crawl space under the base floor.
80_Finnish_Health-Humidity | The crawl space must be ventilated.
81_Finnish_Health-Humidity | Moisture in the crawl space must not damage the functionality or durability of structures.
83_Finnish_Health-Humidity | In a new building, the crawl space height must be 0.8 metres on average at the minimum.
84_Finnish_Health-Humidity | The crawl space must be accessible for inspections and maintenance of the equipment and systems located there.
86_Finnish_Health-Humidity | The structure of the exterior wall against the ground must be waterproofed or isolated against water pressure or a structurally managed water removal system allowing the cellar wall to dry in an outward direction must be used to prevent moisture from the surrounding ground and storm water from penetrating the wall structure.
87_Finnish_Health-Humidity | Waterproofing or water pressure barrier must be located on the outer surface of the exterior wall structure against the ground or inside the exterior thermal insulation facing the ground.
97_Finnish_Health-Humidity | If air barriers or vapour barriers have been used in the structure, the seams, edges and penetrations must be tight.
103_Finnish_Health-Humidity | The roof structures and joints must be properly inclined and sealed for water drainage.
105_Finnish_Health-Humidity | The layers of attic floor structures and the ventilation must prevent the accumulation of damaging moisture into the roof structure resulting from water vapour diffusion or airflow.
106_Finnish_Health-Humidity | If air barriers or vapour barriers have been used in the structure, the seams, edges and penetrations must be tight.
109_Finnish_Health-Humidity | Water must not drift into or migrate as a capillary flow from the wet rooms to the surrounding structures and rooms.
110_Finnish_Health-Humidity | Constructions behind surfaces exposed to running water, repetitious splash water or water condensation must be waterproofed.
111_Finnish_Health-Humidity | The flooring and wall covering must provide waterproofing, or separate waterproofing must be installed under the flooring and behind the wall covering.
113_Finnish_Health-Humidity | Wet room waterproofing must form a whole which is impermeable on all waterproofed surfaces as well as on their seams, penetrations and joints.
114_Finnish_Health-Humidity | The flooring functioning as waterproofing or waterproofing located underneath the flooring in wet rooms must have a watertight connection with the waterproofing of the wall.
115_Finnish_Health-Humidity | The structures of the wet rooms must be rigid enough that the thermal and moisture movements do no damage the wet room waterproofing or surface structures.
118_Finnish_Health-Humidity | The slope of the wet room floor must allow water to flow into the floor drain.
119_Finnish_Health-Humidity | The joint between waterproofing and the floor drain must be tight.
33_Finnish_Health-IndoorClimateAndVentilation | A temperature of 21 C shall be used as the design value for room temperature during the heating season.
48_Finnish_Health-IndoorClimateAndVentilation | In a mechanical system, there shall be a clearly labelled stop switch, which shall be located in an easily accessible place.
49_Finnish_Health-IndoorClimateAndVentilation | In a natural ventilation system, the ventilation valves shall be easy to close.
61_Finnish_Health-IndoorClimateAndVentilation | The air flows shall be designed so that the average carbon monoxide concentration in a parking garage for motor vehicles during the hour of use assessed as the most critical does not exceed 35 mg/m3 (30 ppm).
62_Finnish_Health-IndoorClimateAndVentilation | Air flows in the continuous working area of a parking garage for motor vehicles shall be designed so that the instantaneous carbon monoxide concentration does not exceed 7 mg/m3 (6 ppm).
73_Finnish_Health-IndoorClimateAndVentilation | Extract air of categories 2, 3 and 4 shall not be used as recirculation air.
77_Finnish_Health-IndoorClimateAndVentilation | When heat is recovered from extract air of category 4, there shall be no leaks between supply and extract air.
81_Finnish_Health-IndoorClimateAndVentilation | The air in a building shall flow from spaces of higher indoor air purity to spaces of lower indoor air purity.
87_Finnish_Health-IndoorClimateAndVentilation | In natural ventilation, the vertical ducts of a single dwelling may not be combined, nor may common vertical ducts of more than one dwelling be used.
90_Finnish_Health-IndoorClimateAndVentilation | Any connection of two or more air handling units to the same duct or chamber shall be designed so that the pressures of the rooms or the directions of air flow between the rooms and in the ductworks do not change when the air flows of the units are being controlled.
91_Finnish_Health-IndoorClimateAndVentilation | A natural ventilation system, a mechanical extract ventilation system or a mechanical supply and extract ventilation system shall not be designed to be combined in such a way that the directions of air flow between the rooms and in the ductworks may change when the air flows are being controlled.
99_Finnish_Health-IndoorClimateAndVentilation | In a mechanical ventilation system, the air handling units and chambers shall be able to withstand the loads caused by fan pressure while the shutoff dampers are closed.
100_Finnish_Health-IndoorClimateAndVentilation | If the cross-sectional area of a mechanical ventilation systems air duct is designed to be greater than 0.06 m2, the outdoor air and exhaust air ducts shall be fitted with shutoff dampers that close automatically when the system shuts down.
55_Finnish_Health-WaterAndSewerage | Products to be used in the water system shall be suitable for conveying household water.
59_Finnish_Health-WaterAndSewerage | The cold water pipe shall be designed and installed so that the temperature in the cold water system may not exceed 20 degrees Celsius.
60_Finnish_Health-WaterAndSewerage | After a period of non-use of at least eight hours, the water temperature may not exceed 24 degrees Celsius.
61_Finnish_Health-WaterAndSewerage | The water temperature of the water in the hot water system shall be at least 55 degrees Celsius and available from the hot water plumbing fixture within 20 seconds.
62_Finnish_Health-WaterAndSewerage | The temperature of the water available from the hot water system may not exceed 65 degrees Celsius.
63_Finnish_Health-WaterAndSewerage | The water system shall be designed so as to prevent detrimental cross-flow of water from the hot water pipe to the cold water pipe or vice versa.
65_Finnish_Health-WaterAndSewerage | The water system shall withstand internal excess pressure of at least 1 000 kilopascals.
67_Finnish_Health-WaterAndSewerage | In connection with repair and alteration work, the heat emitters connected to the domestic hot water ring duct may be replaced so that the heat emission capacity of the heat emitters to be installed does not exceed 200 Watts per room.
71_Finnish_Health-WaterAndSewerage | The structure of the control appliance of the plumbing fixture shall be such that its surface temperature does not arise above 40 degrees Celsius.
73_Finnish_Health-WaterAndSewerage | The water meter of a property shall be located in a place where it is easy to install, read and service and where it cannot freeze.
75_Finnish_Health-WaterAndSewerage | The apartment-specific water meters shall be located in a place where they are easy to install, read and service.
81_Finnish_Health-WaterAndSewerage | In order to detect water leaks, structural solutions that direct the leaked water in sight shall be used.
82_Finnish_Health-WaterAndSewerage | Vertical service pipes shall be equipped with mechanical or structural leak detectors at each floor if the service pipes are not visible.
84_Finnish_Health-WaterAndSewerage | The water system shall be leakproof.
86_Finnish_Health-WaterAndSewerage | Water pipes that are located in cold premises shall be thermally insulated.
89_Finnish_Health-WaterAndSewerage | The supports and fastening points of water pipes shall be such that neither heat expansion nor forces generated by water flow cause the pipes to shift, loosen, break or make disturbing noises.
93_Finnish_Health-WaterAndSewerage | The shutoff valves shall be located: 1) at each house; 2) at each apartment; 3) in vertical service pipes; 4) on both sides of devices installed in the service pipes; 5) before a device or fixture that is connected to the connector pipe; 6) on both sides of the water meters.
94_Finnish_Health-WaterAndSewerage | The domestic hot water equipment shall have a safety device to prevent excess pressure.
97_Finnish_Health-WaterAndSewerage | The water system shall incorporate: 1) a pressure gauge; 2) thermometers in the water pipe of mixed domestic hot water from the water heater and in the domestic hot water ring duct to measure the temperature of return water; 3) throttling valves.
102_Finnish_Health-WaterAndSewerage | The booster equipment shall be fitted with regulating devices to control the outlet pressure so that no disturbing pressure fluctuations or noises are generated as well as with safety fittings to prevent excessively high overpressure.
106_Finnish_Health-WaterAndSewerage | The integrity of the water system shall be ensured with pressure testing using water.
107_Finnish_Health-WaterAndSewerage | The test shall be carried out so that the water pipes and their joints are uninsulated and easily visible.
111_Finnish_Health-WaterAndSewerage | The flushing shall be carried out with household water to remove any dirt and debris from the pipe network.
122_Finnish_Health-WaterAndSewerage | Waste water shall be conveyed to the sewer of the water supply plant or for purification property-specifically or to a cesspit.
124_Finnish_Health-WaterAndSewerage | A water point shall incorporate a drainage point that is connected to the sewer via a drainage fixture.
125_Finnish_Health-WaterAndSewerage | No more than two drainage wells may be connected to a floor drain and they may be located at a maximum distance of three meters from the floor drain.
126_Finnish_Health-WaterAndSewerage | In the construction of a new building as well as in repair and alteration work corresponding to the construction of a new building, the premises to be fitted with a floor drain shall be: 1. showers and bathrooms as well as wash rooms in connection with saunas; 2. laundry room; 3. heat distribution room; 4. ventilation unit room; 5. toilet facility intended for public use; 6. technical utility room with a possibility to water damage; 7. car wash facility; 8. special facilities cleansed by water rinsing.
128_Finnish_Health-WaterAndSewerage | If waste water cannot be conveyed from the drainage points of a building with gravity unloading via a gradient sewer, the waste water shall be pumped.
129_Finnish_Health-WaterAndSewerage | The pumping station shall be water tight and resistant to earth pressure and it may not cause odour problem.
130_Finnish_Health-WaterAndSewerage | The waste water pumping station shall be ventilated.
131_Finnish_Health-WaterAndSewerage | The pumping station shall be equipped with a malfunction detector.
132_Finnish_Health-WaterAndSewerage | The pumping station shall be located in a place where it can be easily inspected and serviced.
133_Finnish_Health-WaterAndSewerage | If a drainage point is located below the height of backwater, the waste water must be pumped.
134_Finnish_Health-WaterAndSewerage | A drainage point shall be equipped with a cleansable water seal.
135_Finnish_Health-WaterAndSewerage | Sewers shall be connected to a stack vent that extends above the roofing of a building.
136_Finnish_Health-WaterAndSewerage | A stack vent located in cold premises shall be thermally insulated.
144_Finnish_Health-WaterAndSewerage | A sewer installed in the ground shall withstand the load imposed by soil, soil corrosion as well as subsidence of soil.
145_Finnish_Health-WaterAndSewerage | Leakage from a pressure sewer located in a groundwater zone shall be detectable.
146_Finnish_Health-WaterAndSewerage | Water pipes and sewers installed in the ground shall be identifiable and they shall be located separate from one another.
149_Finnish_Health-WaterAndSewerage | The materials and fittings shall be compatible.
152_Finnish_Health-WaterAndSewerage | If sand, sludge, grease, petrol, oil or other detrimental physical or chemical substances may end up in the sewerage system or network or in the environment, the sewerage system shall be equipped with a separator or treatment device.
153_Finnish_Health-WaterAndSewerage | The separator devices shall be located so that they can be serviced and emptied easily and without causing problems.
154_Finnish_Health-WaterAndSewerage | The oil and grease separators shall be equipped with a filling alarm.
157_Finnish_Health-WaterAndSewerage | The sewerage system shall be equipped with cleanouts that are easy to handle and lockable in both horizontal and vertical sewers.
158_Finnish_Health-WaterAndSewerage | The cleanouts shall be located so that the entire pipeline may be cleansed.
165_Finnish_Health-WaterAndSewerage | The storm water system shall be cleansable via manholes and fittings.
169_Finnish_Health-WaterAndSewerage | The storm water sewers within the building shall be equipped with condensation insulation.
172_Finnish_Health-WaterAndSewerage | Drains shall convey foundation drainage water via drainage wells to a collection well.
13_Finnish_SafetyOfUse | Staircases must be safe, sufficiently spacious and suitable for their purpose.
14_Finnish_SafetyOfUse | The surface of stairs the must not be slippery.
17_Finnish_SafetyOfUse | The stairs between floor levels must be covered.
18_Finnish_SafetyOfUse | If a residential block of flats does not have a lift, the stairs between floor levels must have natural light and at least one intermediate landing.
21_Finnish_SafetyOfUse | In the entrance halls and other indoor areas of administrative, service and business premises and in assembly areas, the riser of the steps must be no more than 160 millimetres and the tread must be no less than 300 millimetres.
22_Finnish_SafetyOfUse | The riser of the indoor steps of dwelling units and living quarters may be no more than 190 millimetres, and the tread must be no less than 250 millimetres.
23_Finnish_SafetyOfUse | The rise of the indoor steps of other spaces intended for everyday use may be no more than 180 millimetres, and the tread must be no less than 270 millimetres.
24_Finnish_SafetyOfUse | If stairs are used only as an emergency exit and if they lead to spaces in a dwelling or accommodation facility other than those that are necessary for living, the riser may be no more than 220 millimetres and the tread must be no less than 220 millimetres.
25_Finnish_SafetyOfUse | The riser of the steps in an exit may be no more than 180 millimetres.
26_Finnish_SafetyOfUse | The tread must be no less than 270 millimetres.
28_Finnish_SafetyOfUse | The tread of steps in covered or heated outdoor staircases must be no less than 300 millimetres, and the riser may be no more than 160 millimetres.
29_Finnish_SafetyOfUse | The tread of steps in uncovered or unheated outdoor staircases must be no less than 390 millimetres, and the riser may be no more than 130 millimetres.
32_Finnish_SafetyOfUse | The side edges of stairs and landings must be fitted with a raised camber to prevent slipping over the edge if a cube measuring more than 50 millimetres in width is able to pass through the opening between the plane level and the handrail or wall.
33_Finnish_SafetyOfUse | The distance between a door that opens onto a landing and the upper edge of the ramp or flight of stairs must be no less than 400 millimetres on the side wall and no less than 1,500 millimetres on the end wall.
34_Finnish_SafetyOfUse | A landing measuring at least 800 millimetres in length must be reserved in front of and behind a door located in an exit route.
39_Finnish_SafetyOfUse | A guardrail must be used at points with a level difference of over 0.7 metres, if these can be accessed by children.
40_Finnish_SafetyOfUse | The protective part of the barrier must extend to a height of at least 0.7 metres from the surface of the landing or step.
41_Finnish_SafetyOfUse | The barrier must not feature horizontal structures or patterns that make it possible to climb.
43_Finnish_SafetyOfUse | The total height of the barrier must be one metre if the drop is no more than six metres.
48_Finnish_SafetyOfUse | If the protective part of the barrier contains only vertical structures, a cube with edges of no more than 100 millimetres may pass through its openings.
50_Finnish_SafetyOfUse | A cube with edges of no more than 200 millimetres may pass between the upper edge of the barrier and the protective part.
51_Finnish_SafetyOfUse | A cube with edges of no more than 50 millimetres may pass between the lower edge of a barriers protective part and the landing or the upper surface or edge of a step.
52_Finnish_SafetyOfUse | A cube of no more than 100 millimetres may pass between the stair steps.
54_Finnish_SafetyOfUse | On stairs and ramps, a handrail must be installed for the entire length and on both sides of the structure.
56_Finnish_SafetyOfUse | A handrail must be designed and shaped so that it allows a firm grip.
57_Finnish_SafetyOfUse | A handrail and its ending must be shaped safely and must continue past the start and end points of the structure.
58_Finnish_SafetyOfUse | The handrail must continue onto the intermediate landing without interruption.
59_Finnish_SafetyOfUse | In public outdoor and indoor spaces, and in business and service premises, a handrail must continue at least 300 millimetres past the start and end points of the structure, and in the case of stairs or ramps that have a width exceeding 2.4 metres and are located in assembly areas, it must also be placed so as to divide the passageway into parts no wider than the abovementioned width.
63_Finnish_SafetyOfUse | The lighting must not cause glare that endangers safety.
65_Finnish_SafetyOfUse | Ramps, steps, thresholds and differences in levels in passageways must be clearly indicated using lighting and surface brightness contrasts or warning signs.
67_Finnish_SafetyOfUse | The breaking of a glass structure or other light-permeable structure of a building must not cause a danger of falling or a danger of injury from fragments falling onto persons below.
69_Finnish_SafetyOfUse | Windows, glass walls and glass doors into which there is a danger of collision must be marked in such a way that they can be easily noticed.
70_Finnish_SafetyOfUse | Their glazing must be made of safety glass.
80_Finnish_SafetyOfUse | In dwellings and other premises that are used by children, restrictors must be installed on windows and other openings where there may be a danger of falling, and these must be such that they limit the easy opening of the window to 100 millimetres.
81_Finnish_SafetyOfUse | Any restrictors placed on windows used as emergency exits must, however, be easily releasable by an adult.
82_Finnish_SafetyOfUse | Ladders and other structural elements at emergency exits and service routes must be designed and constructed so that they can also be used in an emergency situation.
83_Finnish_SafetyOfUse | The free opening of the vertical hatch or window of an emergency exit must be at least 600 millimetres in height and 500 millimetres in width; however, the sum of these must be at least 1,500 millimetres.
84_Finnish_SafetyOfUse | The opening of a horizontal hatch must be at least 600 x 600 millimetres.
87_Finnish_SafetyOfUse | The driveway and parking area at a plot or building site must be separated from pedestrian, play and recreation areas.
88_Finnish_SafetyOfUse | A driveway must not intersect a walkway leading to a play area.
90_Finnish_SafetyOfUse | Routes intended for vehicle traffic must be located in a way that does not restrict pedestrian routes or the space required for opening doors and gates.
96_Finnish_SafetyOfUse | Entrances and passageways to playgrounds and recreation areas used in the wintertime, as well as street areas surrounding the building and other public areas, must be protected from snow and ice falling from the roof of the building using snow barriers, taking into account the pitch of the roof.
99_Finnish_SafetyOfUse | The free height from the ground or from the surface of a driveway or walkway of the lower edge of a structural element, device or equipment protruding from the building, such as a balcony, bay window, sign, lighting device or awning, must be at least 2.2 metres, unless the area is protected so as to prevent the danger of collision.
103_Finnish_SafetyOfUse | In rooms with no fixed seats or furnishings, the number of persons shall be calculated to be two persons per square metre.
105_Finnish_SafetyOfUse | Seats must be fixed to a base if the floor of the seating area is sloped or if there are level differences between the floors of the respective rows of seats.
106_Finnish_SafetyOfUse | If there are more than 60 chairs in a space, they must be linked to one another in at least four groups, unless the chairs are placed around tables.
107_Finnish_SafetyOfUse | Fixed or linked seats must be arranged as rows of seating with an access route on the side of the rows.
111_Finnish_SafetyOfUse | The depth of standing rows must be at least half a metre.
114_Finnish_SafetyOfUse | The access route in the seating area or standing auditorium must be directly accessible from the end of each row.
115_Finnish_SafetyOfUse | The width of access routes in assembly areas with a maximum capacity of 60 persons must be at least 900 millimetres.
116_Finnish_SafetyOfUse | In spaces intended for more than 60 persons, the width of the access route must be at least 1,200 millimetres.
119_Finnish_SafetyOfUse | The slope of the floor surface in the seating area and access route may not exceed 8 per cent (1:12.5).
124_Finnish_SafetyOfUse | There must be safe and easily accessible, uninterrupted access routes to any chimneys, ventilation equipment and other building equipment and structural elements that are located on the roof of the building and that must be accessed regularly.
126_Finnish_SafetyOfUse | In buildings more than 9 metres and at most 28 metres in height, the attic and roof must be accessible via the interior and exterior of the building; in buildings more than 28 metres in height, these must be accessible via the interior.
127_Finnish_SafetyOfUse | A building with a height exceeding 9 metres must be equipped with anchoring structures for safety lines.
12_Finnish_StabilityOfStructures | For continuing horizontal structures the loaded area shall be calculated span by span.
13_Finnish_StabilityOfStructures | Joints between vertical and horizontal structures shall always be designed without a reduction factor.
16_Finnish_StabilityOfStructures | The reduction factor Î±n shall not be applied together with a combination factor Ïˆ or reduction factor Î±A.
25_Finnish_StabilityOfStructures | When a warning sign is not posted, the areas shall be designed to an axle load Qk and also to an axle group load equal to 190 kN.
30_Finnish_StabilityOfStructures | Parapets in categories A to E and panel parts of walls acting as parapets, as well as their fasteners, shall be designed to the concentrated load Qk = 0.3 kN acting on a random spot.
61_Finnish_StabilityOfStructures | For large roofs, where the smaller horizontal dimension of the roof is 50 m or more, and the topography is windswept, the value of the exposure coefficient shall be at least 1.
95_Finnish_StabilityOfStructures | The minimum shade air temperatures represent values with an annual probability of falling below of 0.02, and the maximum shade air temperatures represent values with an annual probability of being exceeded of 0.02.
96_Finnish_StabilityOfStructures | The values of shade air temperature may be adjusted for height above sea level by subtracting 0.5°C per 100 m of height for minimum shade air temperatures and 1.0Â°C per 100 m of height for maximum shade air temperatures.
175_Finnish_StabilityOfStructures | At least 30% of the ties shall be located in the immediate vicinity of the grid lines of the columns and the walls.
179_Finnish_StabilityOfStructures | If the internal ties must be centred on the supporting line, the minimum value of the tie force, 70 kN, will also be applied to internal ties.
180_Finnish_StabilityOfStructures | If the internal ties must be centred on the supporting line, the minimum value of the tie force, 10 kN, will also be applied to internal ties.
186_Finnish_StabilityOfStructures | Edge columns and walls shall be tied to every floor and roof.
194_Finnish_StabilityOfStructures | Each column and wall shall be supplied with continuous vertical ties from the foundations to the roof level.
229_Finnish_StabilityOfStructures | The inaccuracies of the crane wheels should be determined together with the crane supplier.
12_Finnish_Accessibility | If parking spaces are provided for a building, an adequate number of them, but at least one, shall be intended for the use of a person with mobility and functional impairment.
19_Finnish_Accessibility | The clear width of the door and opening leading to room spaces of a non-residential building as well as to residential rooms of a residential building, necessary spaces serving residence and spaces serving the use of the building shall be at least 800 millimetres.
44_Finnish_Accessibility | In addition, on one side of the toilet seat there shall be a free space of at least 800 millimetres.
55_Finnish_Accessibility | In addition, on both sides of the toilet seat there shall be a free space of at least 800 millimetres.
56_Finnish_Accessibility | Alternatively, two toilet facilities can be placed close to each other, one of them with a free space of at least 800 millimetres on the left side of the toilet seat and the other on the right side of the toilet seat.
135_Finnish_FireSafety | If the free gap between facing walls of adjacent glazed balconies or the distance of the wall to the window of an adjacent fire compartment is less than 2 metres, the wall in question must be class EI 15.
54_Finnish_Health-IndoorClimateAndVentilation | The outdoor air flow of a dwelling unit, however, shall be designed to be a minimum of 18 dm3/s.
84_Finnish_Health-IndoorClimateAndVentilation | If the air flows of extract air categories 1 and 2 are combined into the same duct and category 2 air flow accounts for more than 10 of the combined air flow, the combined air flow is classified under category 2.
130_Finnish_Health-IndoorClimateAndVentilation | extract air of category 3 shall be conducted through individual ducts, or common ducts serving spaces of the same type as regards level of air purity, to the outdoors, into a collection duct installed above the spaces it serves or into an extract air chamber.
85_Finnish_Health-IndoorClimateAndVentilation | Extract air from toilets, washrooms and cleaning spaces may be conducted to vertical ducts for extract air categories 1 and 2 if the total extract air flow from these spaces does not exceed 10 of the total air flow in the vertical duct.
88_Finnish_Health-IndoorClimateAndVentilation | extract air of category 4 shall be conducted to the outdoors through individual extract air ducts.
97_Finnish_Health-IndoorClimateAndVentilation | Extract air ducts in extract air categories 1 and 2 may, however, be at positive pressure within the building, provided that the ductwork is at least of airtightness class C.
131_Finnish_Health-IndoorClimateAndVentilation | Extract air ducts in extract air category 3 and exhaust air ducts for individual dwelling units may be at positive pressure within the building, provided that the ductwork is at least of airtightness class D.
132_Finnish_Health-IndoorClimateAndVentilation | Extract air ducts in extract air category 4 may be at positive pressure within the building if the ductwork does not leak.
15_Finnish_SafetyOfUse | All evacuation areas must be designed in such a way that it is possible to transport an immobile individual on a stretcher via the exit route.
45_Finnish_SafetyOfUse | The height of a barrier in a dwellings indoor areas may, however, be at least 0.9 metres if the drop is less than three metres.
49_Finnish_SafetyOfUse | However, a horizontal gap in a protective part must be no higher than ten millimetres.
97_Finnish_SafetyOfUse | In addition, the entrance must be protected against snow loads with a covering.
109_Finnish_SafetyOfUse | Level differences of over 500 millimetres must be equipped with an appropriate safety barrier, railing or handrail.
136_Finnish_SafetyOfUse | Barriers on loading docks must not impede loading and unloading.
110_Finnish_StabilityOfStructures | However, when the snow load can occur, the minimum value of the load s should be at least 0.5 kN/m2.